## WORKSHEET (2)
500 Gould Drive, Cookeville, TN 38506 ¦ www.tutco.com
Date: |  |  |  | Contact Name:
Company: |  |  |  | Contact Phone:
Job: |  |  |  | Contact Email:
What Do I Need to Know to Quote or Order a Duct Heater?
DUCT TYPE |  | RECTANGULAR |  |  | ROUND
Duct Size |  | Height |  |  | Diameter
Width
Slip In or Flange Mount
Is the duct internally insulated
If so, how thick is the Insulation? Note: Set Recess Equal to the Internal Insulation Thickness
Left Hand or Right Hand Offset Control Box?
KW Required
Voltage Required
Phase Required
Stages Required
Control Voltage Required
What Accessories or Options are Required? (See Catalog or Submittal for Details)
| Gasketed Cover* |  | Power Fusing (Std.for htrs > 48A) |  |  | Pilot Light-Heater Energized*
| 80/20 A-Wire |  | Fan Interlock Relay* |  |  | Pilot Light-Stage Energized*
| Stainless Steel Terminals |  | Airflow Switch |  |  | Pilot Light-A.F. Switch Open*
| Vapor Barrier* |  | Adjustable Airflow Switch* |  |  | Disconnect Switch+
| Derated Coil-35 Watt Density* |  | Transformer |  |  | SCR+
| Derated Coil-25 Watt Density* |  | Transformer Fusing-Primary |  |  | Electronic Step Controller*+
| Recessed Terminal Box |  | Transformer Fusing-Secondary |  |  | Room Thermostat
|  |  | Time Delay* |  |  | Duct Thermostat
*=Not Available on Round Duct Heaters +=Not Available on Bottom Mount Duct Heaters
Custom Build Options:
| VAV Heater |  | Outdoor Rated |  |  | Remote Panel
| Bottom Mount |  | Vertical Mount |  |  | Plenum Discharge
Special Notes/Requirements:
Notes:
1. Please see the installation instructions for installation details and restrictions. 2. For slip in heaters being installed into an internally insulated duct, decrease the height by 2 times the insulation thickness, decrease the width by the insulation thickness, and add a recess equal to the insulation thickness. 3. All heaters will require either a fan relay or an airflow switch per UL requirements. If neither is chosen, a fan relay will be specified. If both a fan relay and airflow switch are required, both must be specified as options/accessories.4. Power fusing is standard on all heaters above 48.0 amps. Power fusing must be specified as an option/accessory if required for heaters rated 48 amps or less.
Phone: (931) 432 - 4141 ¦ Fax: (931) 432 - 4140 ¦ Email: customerservice@tutco.com

## Sheet1
Mount | Insulation | L-R
Slip-in | No | Left
Flange | Yes | Right